Installation of

Nut v0.45.4-1 on Linux with the APC BackUPS Pro 280VA

(v1.0, 27Sept2002)

This How-To explains the steps involved in setting up a Dell or Penguin computer system with Red Hat Linux v7.3 for use with the APC BackUPS Pro 280VA uninterruptible power supply (UPS) and Network UPS Tools (NUT) software. The document is divided into 7 sections:

1. Requirements

2. Hardware Configuration

3. Software, Part 1 (installation and configuration)

4. OS Configuration

5. Software, Part 2 (configuration)

6. Testing

7. Troubleshooting

1. Requirements:

Red Hat Linux v7.3 (RH7.1)

nut-0.45.4-1.i386.rpm

nut-client-0.45.4-1.i386.rpm

nut-cgi-0.45.4-1.i386.rpm

APC BackUPS Pro 280VA

APC UPS cable (PN: 940-0095B)

Note that the version of NUT listed here is has been tested and found to work with RedHat v7.3. It has not been tested on older systems so compatibility is uncertain.

New and/or beta versions of NUT are available for download at:

http://www.exploits.org/nut

2. Hardware Configuration

Make available one COM port and connect the UPS using the APC UPS cable with part number 940-0095B. The cable should have been supplied with the UPS unit. Otherwise request one from APC and they will send it out free of charge.

Turn the computer on and enter the bios settings display. Shortly after you power on the computer system you should see a brief message showing how to do this. Usually, depressing the F2 or Delete key during the boot process will get you there.

Once in, look for power settings and ensure that the following requirement is met:

state after AC power failure should be ON upon power restore

Save the change and continue booting.

3. Software Installation and Configuration, Part 1 (install)

Log in as root.

Obtain the following nut rpm files from the UNAVCO software download site:

1. nut-client-0.45.4-1.i386.rpm

2. nut-0.45.4-1.i386.rpm

3. nut-cgi-0.45.4-1.i386.rpm

Install the rpm files in the order listed above as follows:

[root@localhost]# rpm -Uvh <nut rpm>

The following files should have been installed:

/etc/ups/hosts.conf             (configuration files)

./multimon.conf

./ups.conf

./upsd.conf

./upsd.users

./upsmon.conf

./upssched.conf

./upsset.conf

/etc/init.d/ups                 (ups service)

/etc/sysconfig/ups              (additional configuration file)

/usr/sbin/upsd                  (ups daemon)

./upsmon                (ups monitor)

./upssched              (event scheduler)

./upssched-cmd          (event scheduler tasks)

/usr/bin/apcsmart               (ups driver)

Note that there are other files that are not listed here that should have been installed. They are drivers for other UPSs  and utilities for functions which will not be used. Some files listed above that are greyed out will not used as well.

4. OS Configuration

Edit system file:

/etc/rc.d/init.d/halt

Just about at the end of file you’ll find these lines:

if [ "$command" = halt ] ; then

if [ -r /etc/ups/upsmon.conf -a -f /etc/killpower -a -f /etc/sysconfig/ups ] ; then

. /etc/sysconfig/ups

[ "$SERVER" = "yes" -a "$MODEL" != "NONE" -a -n "$MODEL" -a -n "$DEVICE" ] && $MODEL -k $DEVICE

fi

fi

Change the line in boldface to:

[ "$SERVER" = "yes" -a "$MODEL" != "NONE" -a -n "$MODEL" -a -n "$DEVICE" ] && $MODEL -a $DEVICE -k

Note that the changes are highlighted in red.

Explanation:

The statements listed above translate to the following:

1. if a ‘halt’ command has been issued

2. check to see if the upsmon, killpower, and ups files exist

3. if they do exist, source the /etc/sysconfig/ups file (the variables that are assigned within

that file are exported to the shell environment.

4. if the group of variables listed in the square brackets meet the conditions stated within

then execute $MODEL -a $DEVICE -k

The last command tells the UPS to shut down. This is the last statement that is executed after the OS itself has sucessfully unmounted the filesystems.

$MODEL is the upsdriver, apcsmart

$DEVICE is the ups as described in /etc/ups.conf

5. Software Installation and Configuration, Part 2 (configuration)

A. Edit file:

/etc/rc.d/init.d/ups

Just short of half-way down you should see these lines:

echo -n $”Starting UPS monitor (master): “

daemon /usr/sbin/upsmon

echo

else

echo -n $”Starting UPS monitor (slave): “

daemon /usr/sbin/upsmon

echo

Add to both lines in boldface such that:

daemon /usr/sbin/upsmon -p

Note that the change is highlighted in red.

Explanation:

The -p flag tells upsmon to run in privileged mode always. In other words, all child processes of upsmon will inheret root privileges from the upsmon parent process. When upsmon (owned by root) is run it will spawn one child process which is owned by the user nobody.

B. Edit file: /etc/sysconfig/ups

Add these lines to the file (everything else may be deleted):

SERVER=yes

MODEL=apcsmart

DEVICE=myups

OPTIONS=”-a”

Explanation:

SERVER: 		The UPS is connected to the same machine that NUT is controlling

MODEL: 		The name of the device driver for the type of UPS being used

DEVICE: 		The name assigned to the UPS. It may be arbitrary but it must be

consistent across all configuration files where applicable.

OPTIONS:		Arguments passed to the device driver (MODEL). -a flag tells the

driver to read the /etc/ups/ups.conf configuration file which contains information on where and how the UPS is connected.

C. Edit file /etc/ups/ups.conf

Add these lines to the file (everything else may be deleted):

[myups]

driver=apcsmart

port=/dev/ttySn

cable=940-0095B

Explanation:

[myups]: 	The name assigned to the UPS. It may be arbitrary but it must be

consistent across all configuration files where applicable. Must be

placed within [].

driver: 	The name of the device driver for the type of UPS being used

port:		The port to which the UPS is connected (e.g., /dev/ttyS1)

cable:	The APC cable with part number 940-0095B. This cable is

required. Although others may work they have not been tested.

The cable type must be specified since the default configuration

assumes a different cable.

D. Edit file /etc/ups/upsd.conf

Add these lines to the file (everything else may be deleted):

ACL all 0.0.0.0/0

ACL localhost 127.0.0.1/32

ACCESS grant master localhost password

ACCESS deny all all

Explanation:

ACL: 		Access Control List. Lists the hosts that may access the server.

ACCESS: 	What level of access to grant, to whom, and what password to

use.

E. Edit file /etc/ups/upsmon.conf

Add or modify existing lines within file to match the following:

MONITOR myups@localhost 1 password master

MINSUPPLIES 1

SHUTDOWNCMD “/sbin/shutdown -h +0”

NOTIFYCMD /usr/sbin/upssched

POLLFREQ 10

POLLFREQALERT 5

HOSTSYNC 15

DEADTIME 15

POWERDOWNFLAG /etc/killpower

UPSNAME myups@locahhost

NOTIFYTYPE ONBATT

NOTIFYFLAG ONBATT SYSLOG+WALL+EXEC

NOTIFYFLAG ONLINE SYSLOG+WALL+EXEC

NOTIFYFLAG LOWBATT SYSLOG+WALL+EXEC

NOTIFYFLAG SHUTDOWN SYSLOG+WALL+EXEC

RBWARNTIME 43200

NOCOMMWARNTIME 300

FINALDELAY 15

Explanation:

MONITOR:		Which UPS to monitor.

MINSUPPLIES:	How many UPSs that are being monitored. Cannot be less than 1.

SHUTDOWNCMD:	Which command to issue for shutdown.

NOTIFYCMD:		Which script to run when an event occurrs (e.g., power failure).

POLLFREQ and POLLFREQALERT:	Polling frequency.

HOSTSYNC:		Only used when NUT is serving more than one system.

DEADTIME:		Time to wait before warning about an unresponsive UPS.

POWERDOWNFLAG:	The file the ups monitoring software will look for when its time to

shutdown. This signals the shutdown process.

UPSNAME:		Name of the ups in the form [upsname]@localhost. Required for upssched.

NOTIFYTYPE		Notify on type of event specified. Required for upssched.

NOTIFYFLAG		On event type (e.g., power failure, back line, etc.) send notification via syslog

(/var/log/messages) or using the unix wall command or run an executable.

RBWARNTIME:		Replace battery warning. Duration before warning in seconds.

NOCOMMWARNTIME:	Amount of time to wait before warning of no communication with UPS.

FINALDELAY:		Time to wait before final shutdown.

F. Edit file /etc/ups/upssched.conf

Add or modify existing lines in the file to match the following:

CMDSCRIPT /usr/sbin/upssched-cmd

PIPEFN /var/run/upssched.pipe

AT ONBATT * START-TIMER onbattwarn 120

AT ONLINE * CANCEL-TIMER onbattwarn

Explanation:

CMDSCRIPT: 	The script or executable  that will perform the actions specified in

this and any other related configuration file

(e.g., /usr/sbin/upssched-cmd).

AT ONBATT/: 	Do action specified when certain condition exists. E.g., when on

ONLINE	battery, start the shutdown timer. When back online, cancel the

shutdown timer.

G. Edit file /usr/sbin/upssched-cmd

Add or modify existing lines in the file to match the following:

#! /bin/sh

case $1 in

onbattwarn)

echo “Utility power failure…shutting down…”; /usr/sbin/upsmon -c fsd

;;

)*

logger -t upssched-cmd “Unrecognized command: $1”

;;

esac

Explanation:

This script is executed during the final stage of system shutdown when the read-only filesystems are remounted. A command is issued to the UPS instructing it to turn off. The computer system and UPS will remain on for about twenty seconds after this command is sent.

H. Remaining Items…

Be sure that ownership/group and permissions for each file is set correctly. They should be as follows:

-rw-------    1 root     root          747 Feb 26  2002 hosts.conf

-rw-------    1 root     root         2174 Feb 26  2002 multimon.conf

-rw-------    1 root     root          441 Sep 27 15:02 ups.conf

-rw-------    1 root     root          465 Sep 27 15:02 upsd.conf

-rw-------    1 root     root         2179 Feb 26  2002 upsd.users

-rw-------    1 root     root          791 Sep 27 15:02 upsmon.conf

-rw-------    1 root     root          535 Sep 27 15:02 upssched.conf

-rw-------    1 root     root         1420 Feb 26  2002 upsset.conf

-rwxr-xr-x    1 root     root         1656 Sep 27 15:02 /etc/init.d/ups

-rwxr-xr-x    1 root     root        19331 Feb 26  2002 /usr/sbin/upssched

-rwxr-xr-x    1 root     root          602 Sep 27 15:02 /usr/sbin/upssched-cmd

-rw-r--r--    1 root     root          412 Sep 27 15:02 /etc/sysconfig/ups

-rwxr-xr-x    1 root     root         5098 Sep 27 15:02 /etc/init.d/halt

Add the new UPS service and activate it in runlevels 3, 4, and 5 by issuing the following commands:

[root@localhost]# /sbin/chkconfig --add ups

[root@localhost]# /sbin/chkconfig --levels 345 ups on

Check to see that it has been turned on:

[root@localhost]# /sbin/chkconfig --list | grep ups

ups            0:off   1:off   2:off   3:on   4:on   5:on    6:off

You are done! Reboot the system and begin testing.

6. Testing

Simulate a power failure to test the machine. Perform the following three tests to confirm a properly working system:

i)   disconnect power, wait for full shutdown (inverter kill), restore power

ii)  disconnect power during bootup, wait for full shutdown, restore power

iii) disconnect power, wait for shutdown process to begin, then restore power during shutdown process

The computer should recover from all these circumstances. Keep in mind the time delays you have set. Impatience may bring about the appearance of a system not working properly. Just wait and see what happens keeping in mind the time delay you set. For the purpose of expediency you may want to temporarily set the shutdown timer to 30 seconds (or less), for example. Just remember to change them back after confirming positive test results. If the system does not appear to be functioning as you would expect, refer to the troubleshooting section of this document.

7. Troubleshooting

| Problem | Remark |
| --- | --- |
| 1. NUT does not appear to install properly or won’t install. | a. Check that the version of rpm file was created for NUT matches rpm installed on the OS. |
| 2. driver does not appear to be communicating with the UPS | a. Make sure you’re using the correct UPS serial cable (940-0095B). b. Did you choose the right UPS driver? c. Is there a port conflict? Make sure the port is available for use. d. Is the UPS plugged into the port? |
| 3. Computer won’t shut down after disconnecting utility power. | a. Did you reboot machine after installing the software? b. Refer to Remarks for Problem #2 |
| 4. Computer powers down completely after disconnecting utility power. Does not reboot automatically after restoring utility power. Must manually turn it back on. | Remove the -p option from the HALTARGS=”HALTARGS -p” line in /etc/rc.d/init.d/halt file. |
| 5. Computer remains on after cutting utility power to the UPS and the UPS inverter shuts down. | Did you plug the computer into the UPS in the first place??? |
| 6. The OS is halted (proper shutdown) and the inverter shuts off after utility power disconnect but after restoring the utility power the UPS turns back on but the computer doesn’t. | Make sure the bios power settings are set so that the computer is on after a power failure recovery. |
| 7. If all else fails… | Contact Jay Sklar via sklarj@ucar.edu |